SECTION 08390

WATERTIGHT DOORS

- GENERAL

  - SECTION INCLUDES

    - EzDam; Model EZD-600

  - RELATED SECTIONS

    - Section 03300 - Cast-In-Place Concrete.

    - Section 04810 - Unit Masonry Assemblies.

    - Section 05120 - Structural Steel.

  - REFERENCES

    - ASTM B 209 - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate.

    - ASTM B 211 - Standard Specification for Aluminum and Aluminum-Alloy Bar, Rod, and Wire.

    - Aluminum Association - Specification for Aluminum Structures, 7th Edition.

    - ASME Structural Welding Code Section IX.

    - FEMA Technical Bulletin 3-93 - Non-Residential Flood Proofing.

    - SEI/ASCE 7-02 - Minimum Design Loads for Buildings and Other Structures.

    - AWS D1.2 - Structural Welding Code - Aluminum.

    - Aluminum Structures - A Guide to Their Specifications and Design.

    - U.S. Army Corps of Engineers, EP 1165-2-314 - Flood Proofing Regulations, 15 December 1995.

  - DESIGN / PERFORMANCE REQUIREMENTS

    - Design watertight EzDam to perform under hydrostatic loads to control short-term load pressures indicated.  All water pressure loads and operating loads are transferred to the building structure.

    - Standard loading: Standard EzDam is designed for hydrostatic loading, and have no additional allowances included for hydrodynamic loads, wave loads or debris impact loads.

  - SUBMITTALS

    - Submit under provisions of Section 01300.

    - Manufacturer's data sheets on each product to be used, including:

      - Preparation instructions and recommendations.

      - Storage and handling requirements and recommendations.

      - Installation instructions.

    - OPTIONAL:  Calculations:  Submit calculations approved by a qualified engineer, to verify the EzDam’s ability to withstand the design loading.

    - Closeout Submittals:  Provide Operation and Maintenance data to include methods for maintaining installed products, precautions against cleaning materials and methods detrimental to finishes and performance.

  - QUALITY ASSURANCE

    - Manufacturer Qualifications: Manufacturer must demonstrate a minimum of five years successful experience in design and manufacture of similar flood related closures. Upon request, provide supporting evidence including list of installations, descriptions, name and method of contact.

    - Welder Qualifications: Welders Certified in accordance with American Welding Society Procedures:  AWS-1-GMAW-S, WPS No. B2.004.90 for applicable material used in production of specified product.

  - DELIVERY, STORAGE, AND HANDLING

    - Store products in manufacturer's unopened packaging container with identification labels intact until ready for installation.

    - Protect materials from exposure to moisture.

    - Store materials in a dry, warm, ventilated weathertight location. If outdoor storage is required, block materials to store at an incline, to prevent pooling of any moisture and promote runoff. Tarp materials in a tent-like arrangement, elevated above the product with open sides to allow airflow. Store all other hardware in a dry controlled environment.

    - Use caution when unloading and handling product to avoid bending, denting, crushing, or other damage to the product.

  - PROJECT CONDITIONS

    - Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results.  Do not install products under environmental conditions outside manufacturer's absolute limits.

  - COORDINATION

    - Coordinate Work with other operations and installation of adjacent materials to avoid damage.

- PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer: PS DOORS, which is located at: 1150 S. 48th Street, Grand Forks, ND 58201; Toll Free Tel: 887-446-1519; Tel: 701-746-4519; Fax: 701-746-8340; Email: 4psinfo@psdoors.com; Web: www.psfloodbarriers.com or www.psdoors.com

    - Substitutions:  Not permitted.

    - Obtain all flood barrier assemblies from single manufacturer.

  - EQUIPMENT

    - Watertight Barriers: Provide the following barriers:

      - EzDam; Model EZD-600

    - Products Details:

      - Sealing Requirements: EzDam and gasket design shall provide an effective against short-term high water situations, to the protection level of 36 inches.

      - Operation:  Manually deployed, latching operable from both sides (typical).

      - Mounting/Load Transfer:  Anchor to existing structure. EzDam designed for specified hydrostatic pressure and will transfer loads to adjacent structure.

      - Frames to be anchored utilizing mechanical anchor types as designed.  Manufacturer to include all anchors and sealants, as designed.

      - Loading Direction to be Positive Pressure Loading; (Direction of loading against EzDam so as to further compress gaskets against flood plank frame-"seating").

      - Provide compression gasket which requires no inflation.

  - MATERIALS

    - EzDam:  Panel to be fabricated from formed aluminum sheets and aluminum tubing, factory welded construction.

    - Gaskets to be factory mounted to flood panel assembly on sides and bottom of panel.  Gaskets to be compressible EPDM rubber type, field replaceable.

    - Jamb Members to be of PS DOORS’ design, members as indicated on drawings, for field installation on existing structure.  Frame members to be fabricated from formed members.

      - Aluminum of appropriate size and strength with welded or mechanical fastened construction.

    - Frame Mounting Hardware: Provide anchors and sealant as required.

    - Operating Hardware:  Include all sealants and hardware necessary for installation, latching and retaining flood barrier as designed.

    - Aluminum products to be mill finish, exposed, interfering welds are ground, not filled or polished.  Exposed welds are factory acid washed, neutralized and rinsed.

    - Warranty:  PS DOORS warrants this product and components to be free from manufacturing defects for a period of One (1) year from date of shipment.

  - FABRICATION

    - Fit and shop assemble items in largest practical sections, for delivery to site.

    - Fabricate items with joints tightly fitted and secured.

    - Supply components required for anchorage of fabrications. Fastener and hardware material and finish as noted on drawings.

- EXECUTION

  - EXAMINATION

    - Do not begin installation until substrates have been properly prepared.

    - If substrate preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

  - PREPARATION

    - Clean surfaces thoroughly prior to installation.

    - Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

  - INSTALLATION

    - Install in accordance with manufacturer's installations instructions, approved shop drawings, shipping, handling, and storage instructions, and product carton instructions for installation.

    - Frames/Jambs shall be installed level, square, plumb, and rigid.

    - Sealants to be applied per product application directions and in accordance with manufacturer's instructions.

    - Tolerances: All dimensional requirements must be in accordance with manufacturer's installation instructions and shop drawings.

    - Field Testing:

      - Perform visual dry test for gasket alignment, continuity contact and pre-compression.

      - Construct temporary water barrier and test installed flood plank.

  - FIELD QUALITY CONTROL

    - Products to be operated and field verified including the sealing surfaces to assure that they maintain contact at the correct sealing points.

    - Verify that latching assemblies operate freely and correctly.

    - Verify all anchorage is in accordance with manufacture's installation instructions and applicable data sheets.

  - CLEANING

    - Repair or replace damaged installed products or components.

    - Clean all sealing surfaces.

    - Touch up damaged finish.

  - PROTECTION

    - Protect installed products until completion of project.

    - Touch-up, repair or replace damaged products before Substantial Completion.

END OF SECTION